### [EQUALS VAV CO] VAV Box – Cooling-Only

The engineer must select:

- Occupied and unoccupied zone temperature setpoints.

- Initial values for all parameters marked adjustable (adj.) to match the application and climate zone.

Refer to the General Sequences of Operation/’Need’ Requests section for details regarding how these requests are sequenced.

#### Zone Temperature Control

##### Temperature Setpoint

Two temperature setpoints apply to the unit: 1) an occupied cooling setpoint equal to [78°F][___][as shown on the Point Schedule] (adj.) plus an adjustable offset from a zone thermostat, and 2) an unoccupied cooling setpoint [83°F][___][as shown on the Point Schedule] (adj.).

##### [YES NC_CO]‘Need Cool’ Request

As zone temperature rises above zone temperature setpoint, send a ‘need cool’ request.

#### Zone Airflow Control

##### Airflow Setpoint

As zone temperature rises above zone temperature setpoint, increase airflow setpoint towards the maximum airflow value [___][as shown on the Point Schedule] (adj.). As zone temperature falls below the zone temperature setpoint, decrease airflow setpoint toward the minimum airflow value [___][as shown on the Point Schedule] (adj.).

##### Primary Air Damper

Modulate the primary air damper to maintain the primary airflow at setpoint.

### [EQUALS VAV RH] VAV Box with Reheat

The engineer must select:

- Occupied and unoccupied zone temperature setpoints.

- Initial values for all parameters marked adjustable (adj.) to match the application and climate zone.

- Hot water or electric heat. Proving airflow for electric resistance heating elements should always be hardwired to the heating element safety contacts per the manufacturer’s instructions.

Apply ASHRAE supply air temperature limits where applicable for warming air to minimize stratification.

Refer to the General Sequences of Operation/’Need’ Requests section for details regarding how these requests are sequenced.

#### Zone Temperature Control

##### Temperature Setpoint

Three independent temperature setpoints apply to the unit: 1) an occupied setpoint equal to [73°F][___][as shown on the Point Schedule] (adj.) plus an adjustable offset from a zone thermostat, 2) an unoccupied heating setpoint [63°F][___][as shown on the Point Schedule] (adj.), and 3) an unoccupied cooling setpoint [83°F][___][as shown on the Point Schedule] (adj.). The occupied heating and cooling setpoints are calculated as described below.

Occupied heating setpoint is equal to the occupied setpoint minus [5°F][___][as shown on the Point Schedule] (adj.) for heating.

Occupied cooling setpoint is equal to the occupied setpoint plus [5°F][___][as shown on the Point Schedule] (adj.) for cooling.

Enable cooling mode whenever the zone temperature is above the effective cooling setpoint. Enable heating mode whenever the zone temperature is below the effective heating setpoint.

##### [YES NC_RH] ‘Need Cool’ Request

If zone temperature is above the effective cooling setpoint, send a ‘need cool’ request.

##### [YES NH_RH] ‘Need Heat’ Request

If zone temperature is above the effective heating setpoint, send a ‘need heat’ request.

#### Zone Airflow Control

##### Airflow Setpoint

There are a minimum airflow limit [___][as shown on the Point Schedule] (adj.) and a maximum airflow limit [___][as shown on the Point Schedule] (adj.).

##### Primary Air Damper

Modulate the primary air damper to maintain the effective primary airflow at setpoint.

##### Cool Mode

Reset the effective primary airflow setpoint towards the maximum limit whenever the zone is in cooling mode. When cooling mode is satisfied, reset the effective primary airflow setpoint towards the minimum.

##### Heat Mode

Maintain the primary airflow setpoint at the minimum flow limit. Reset the effective primary airflow setpoint towards the maximum limit whenever the heating is at maximum and zone temperature is still below the heating setpoint. When the heating mode is satisfied, reset the effective primary airflow setpoint towards the minimum limit.

#### Heating Control

##### [EQUALS TERM_HT_RH HW] Hot Water Heating Coil

Modulate the heating hot water coil valve to maintain the zone temperature at the effective heating mode temperature setpoint whenever the zone is in heating mode. Otherwise, command the heating hot water valve closed.

##### [EQUALS TERM_HT_RH ELEC] Electric Heat

Enable electric heat when airflow is proven, otherwise disable electric heat via hardware logic. Stage the electric heat to maintain the zone temperature at the effective heating mode temperature setpoint whenever the zone is in heating mode. Otherwise command the electric heat off.

### [ANY VAV PFBCV SFBCV] VAV Box –Fan-Powered

The engineer must select:

- Occupied and unoccupied zone temperature setpoints.

- Initial values for all parameters marked adjustable (adj.) to match the application and climate zone.

- Hot water or electric heat. Proving airflow for electric resistance heating elements should always be hardwired to the heating element safety contacts per the manufacturer’s instructions.

- Series or parallel fan-powered configuration.

Apply ASHRAE supply air temperature limits where applicable for warming air to minimize stratification.

Refer to the General Sequences of Operation/’Need’ Requests section for details regarding how these requests are sequenced.

#### Zone Temperature Control

##### Temperature Setpoint

Three independent temperature setpoints apply to the unit: 1) an occupied setpoint equal to [73°F][___][as shown on the Point Schedule] (adj.) plus an adjustable offset from a zone thermostat, 2) an unoccupied heating setpoint [63°F][___][as shown on the Point Schedule] (adj.), and 3) an unoccupied cooling setpoint [83°F][___][as shown on the Point Schedule] (adj.). The occupied heating and cooling setpoints are calculated as described below.

Occupied heating setpoint is equal to the occupied setpoint minus [5°F][___][as shown on the Point Schedule] (adj.) for heating.

Occupied cooling setpoint is equal to the occupied setpoint plus [5°F][___][as shown on the Point Schedule] (adj.) for cooling.

Enable cooling mode whenever the zone temperature is above the effective cooling setpoint. Enable heating mode whenever the zone temperature is below the effective heating setpoint.

##### [OR [YES NC_PFBCV] [YES NC_SFBCV]] ‘Need Cool’ Request

If zone temperature is above the effective cooling setpoint, send a ‘need cool’ request.

##### [OR [YES NH_PFBCV] [YES NH_SFBCV]] ‘Need Heat’ Request

If zone temperature is above the effective heating setpoint, send a ‘need heat’ request.

#### Zone Airflow Control

##### Airflow Setpoint

There is a minimum airflow limit [___][as shown on the Point Schedule] (adj.) and a maximum airflow limit [___][as shown on the Point Schedule] (adj.).

##### Primary Air Damper

Command the primary air damper closed whenever the air handler serving this box is deenergized. When the air handler is energized and the fan has been operational for at least [5 sec][___][as shown on the Point Schedule] (adj.), modulate the primary air damper to maintain the primary airflow at the effective primary airflow setpoint.

##### Cool Mode

Reset the effective primary airflow setpoint towards the maximum limit whenever the zone is in cooling mode. When cooling mode is satisfied, reset the effective primary airflow setpoint towards the minimum limit.

##### Heat Mode

Maintain the primary airflow setpoint at the minimum flow limit. Reset the effective primary airflow setpoint towards the maximum limit whenever the heating is at maximum and zone temperature is still below the heating setpoint. When the heating mode is satisfied, reset the effective primary airflow setpoint towards the minimum limit.

#### Heating Control

##### [OR [EQUALS TERM_HT_PFBCV HW] [EQUALS TERM_HT_SFBCV HW]] Hot Water Heating Coil

Modulate the heating hot water coil valve to maintain the zone temperature at the effective heating mode temperature setpoint whenever the zone is in heating mode. Otherwise, command the heating hot water valve closed.

##### [OR [EQUALS TERM_HT_PFBCV ELEC] [EQUALS TERM_HT_SFBCV ELEC]] Electric Heat

Enable electric heat when airflow is proven, otherwise disable electric heat via hardware logic. Stage the electric heat to maintain the zone temperature at the effective heating mode temperature setpoint whenever the zone is in heating mode. Otherwise command the electric heat off.

#### Fan Control

##### [EQUALS VAV SFBCV] Series Fan Start/Stop

Command the fan to run whenever the air handler serving this box is energized or the zone temperature is below the unoccupied heating setpoint. Command the fan off when the air handler is off and zone temperature is above the unoccupied heating setpoint.

##### [EQUALS VAV PFBCV] Parallel Fan Start/Stop

Command the fan to run whenever the zone is in heating mode. Command the fan off when the zone temperature is above the unoccupied heating setpoint.

##### Proof

If the fan is not proven on within [30 sec][___][as shown on the Point Schedule] (adj.) after being commanded to start, generate an alarm.

| Short ID | Description |
| --- | --- |
| VAV | Terminal Unit |
| CO | Cooling-Only VAV |
| RH | VAV with Reheat |
| SFBCV | Series Fan-Powered, Constant Volume |
| PFBCV | Parallel Fan-Powered, Constant Volume |
| TERM_HT | Terminal Heat Source |
| HW | Hot Water Heating Coil |
| ELEC | Electric Heat |
| NC | ‘Need Cool’ Request |
| Yes |  |
| No |  |
| NH | ‘Need Heat’ Request |
| Yes |  |
| No |  |